## Instructions
FOR NOₓ AND CO READINGS
| Span Concentration | Concentration of the span gas used. It must fit within the 50/200 range as explained on the worksheet
| Pre-test Span | The reading with the span gas before you begin the tune-up
| Post-test Span | The reading with the span gas after you finish the tune-up
* | Pre-test Zero | The reading with ambient air before you begin the tune-up. This assumes that ambient air has neglible NOₓ or CO
* | Post-test Zero | The reading with ambient air after you finish the tune-up. This assumes that ambient air has neglible NOₓ or CO
The zero readings should be as close to zero as possible.
FOR OXYGEN READINGS
| Span Concentration | If your span gas contains oxygen, then enter it here. Otherwise, use ambeint air and a default value of 20.9
| Pre-test Span | The reading with ambient air before you begin the tune-up
| Post-test Span | The reading with ambient air after you finish the tune-up
* | Pre-test Zero | The reading with the span gas before you begin the tune-up. This assumes that your span gas has negligible O₂
* | Post-test Zero | The reading with the span gas after you finish the tune-up. This assumes that your span gas has negligible O₂
*The zero readings should be as close to zero as possible.
**Note on Oxygen Reading
The first row on the machine is the zero reading, not the span reading. The oxygen reading with ambient air should be 20.9.
Facility Permit Information
If you do not have the information from the facility, most of the facilities' permits can be found on the SWCAA website: http://www.swcleanair.org/FacilitySrch.asp
Or call the facility representative at SWCAA: 360-574-3058
40 CFR 63 Subpart JJJJJJ (Boiler MACT) Monitoring Requirements for Liquid and Solid Fueled Boilers - Must be completed a minimum of every 2 years
This does not need to be performed or documented for natural gas only combustion units. If a unit is capable of firing a fuel other than natural gas then Subpart JJJJJJ applies.
Refer to the EPA website for more details on compliance at this address http://www.epa.gov/boilercompliance
Person performing the Subpart JJJJJJ inspection and certification should sign and date in the Test Notes box.
NOₓ and CO values should be recorded UNCORRECTED - NO auto 3% correction. The data sheet will provide O₂ correction as well as drift and zero correction.
Notes on Individual Fields on the Monitoring Data Sheet
| Facility Name | This is the name of the facility - best if it matches the list on the SWCAA web page due to similarity of names
| SWCAA ID | This is the SWCAA assigned facility ID and is unique to every facility - again this can be found on the SWCAA website
| Emission Unit ID | This is the SWCAA or facility name tag on the combustion unit - this will be identified in the SWCAA permit and/or by name tag on the unit - important to get this correct. This is NOT the L&I ID or Boiler inspector ID.
| Boiler manufacturer | This is the manufacturers name of the BOILER - not the burner
| Boiler Model Number | This is the BOILER manufacturers model number usually listed on the manufacturer applied name tag
| Boiler Serial Number | This is the manufacturers BOILER serial number usually listed on the manufacturer applied name tag
| Burner Manufacturer | This is the manufacturer of the BURNER - many times it is different than the boiler but not always
| Burner Model Number | This is the BURNER manufacturers model number usually listed on the manufacturer name tag on the BURNER
| Burner Serial Number | This is the BURNER manufacturers serial number usually listed on the manufacturer name tag on the BURNER
| Fuel Type | This cell has a COMBO BOX to select the fuel type - best if the combo box is used.
| Design Firing Rate | This data is usually found on the boiler name plate - if not there then it can be found in the SWCAA Technical Support Document (TSD) for the permit. The MMBtu/hr stands for million Btu per hour - use correct decimals.
| Tested Firing Rate | This field is sometimes difficult to fill in because there is usually no fuel meter. In this case indicate high fire or maximum or medium, etc
| Stack Temperature | This temperature is more important when firing rate is unknown - it many times provides an indication of firing rate and can be used to diagnose emission issues. ALWAYS record. It is auto generated on the form by filling in the individual temperatures as monitored.
| Time of Pre-Test Calibration |  | The monitoring procedure requires that pre and post calibrations be performed within 12 hours of each other - if not the data may be invalidated.
Time of Post-Test Calibration
Does the Permit have a NOₓ or CO Limit?
If yes note the permit number and limit in the boxes below the question. These limits are used to trigger WARNINGS in the WARNING BOX
If no, leave blank - self defeating if you do not enter numbers when the permit has limits. If there is a question call SWCAA.
In the Data box
| AS FOUND line | This is a single set of values for Temp, NOₓ, CO and O₂ - required only for Subpart JJJJJJ - can also be provided for other units - no adjustments should be made to the combustion unit before taking this reading.
The combustion unit should be warmed up and at high fire before taking this reading.
If the combustion unit is not within permit limits, adjustments should be made to bring the combusiton unit into compliance. Recheck as many times as needed to bring unit into compliance.
When the unit is capable of maintaining compliant emission levels, the final set of readings should be recorded on the log sheet - these data would be the AS LEFT condition and should reflect compliant levels.
If the unit can not be adjusted to achieve compliant emission levels, call SWCAA for guidance.
A minimum of 10 readings 30 seconds apart (5 minutes) is necessary to get a valid average test result. More data may be recorded if desired.
Combustion analyzer tapes should be printed and maintained for each combustion unit. The tapes should be annotated to indicate which run they coincide with and which combustion unit.
The recording strips (tapes) should be attached to a piece of paper and copied or scanned to be sent to SWCAA - the facility should maintain the original tapes.

## Monitoring Data Sheet
Southwest Clean Air Agency - Combustion Monitoring Worksheet - O₂ Basis
| Facility Name: |  |  |  | SWCAA ID: | Date Performed:
| Emission Unit ID: |  |  |  | 1. The CO and NOₓ span gas concentrations must not be less than 50% of the target/permitted pollutant concentration nor more than 200% of the target/permitted pollutant concentration. A lower concentration span gas may be used if it is more representative of measured concentrations. 2. The response check is failed if the difference between the pre-test and post-test readings is greater than 10% of the initial span value. 3. The calibration error check is failed if the pre-test analyzer response to a span or zero gas differs from the span or zero value by more than 10% of the span gas concentration. 4. No more than 12 hours may elapse between the pre-test and post- test analyzer response checks. 5. Calibration and use of an NO₂ cell is required, if: • There are significant quantities of NO₂ expected (e.g., specific types of catalysts, afterburners, etc.), or • The combustion analyzer does not have an integral or supplemental NO₂ to NO converter. 6. Submit results to SWCAA within 15 calendar days of monitoring. 7. Include available documentation of monitoring and quality assurance results such as printouts ("tapes"), data log files, span gas cylinder calibrations, calculations, etc.
Combust. Unit Manufacturer:
Combust. Unit Model No:
Combust. Unit Serial No:
Burner Manufacturer:
Burner Model No:
Burner Serial Number:
Monitoring Company:
Analyst Name:
Test Instrument Make:
Test Instrument Model:
Fuel Type:
| Design Firing Rate: |  | MMBtu/hr
| Tested Firing Rate: |  | MMBtu/hr
Time of Pre-Test Calibration:
Time of Post-Test Calibration:
Does the permit have ppm limits for CO and NOₓ?
|  | NOX Limit | CO Limit | O₂ Correction | 40 CFR 63 Subpart JJJJJJ (Boiler MACT) Monitoring Requirements for Liquid and Solid Fueled Boilers
Permit Number |  | (ppm) | (ppm) | (%)
[5 empty] | Was the burner inspected? |  |  | *
[5 empty] | Was the flame pattern inspected and optimized? |  |  | *
Quality Assurance Results |  | NOX (ppm) | CO (ppm) | O₂ (%) | Was the air-to-fuel ratio system operating properly? |  |  | *
[5 empty] | Were total CO emissions optimized? |  |  | *
Span Concentration:
| Pre-Test Span Reading: |  |  |  | Describe any maintenance performed on the burner or boiler system in the "Test Notes" section.
Post-Test Span Reading:
Pre-Test Zero Reading:
| Post-Test Zero Reading: |  |  |  | Test Notes:
Results (Record at least once every 30 seconds for 5 minutes)
Sample | Stack Temp (°F) | NOX Reading (ppm) | CO Reading (ppm) | O₂ Reading (%)
As Found
1
2
3
4
5
6
7 |  |  |  |  | NOTIFICATIONS:
8
9
10
11
12
13
14
15
16
17
18
19
20
Test Averages: | No Data | No Data | No Data | No Data
Drift Corrected Values: |  | No Span | No Span | No Span
Oxygen Corrected Values: |  | No Span | No Span
Questions? - Call the Southwest Clean Air Agency at 360-574-3058 | [6 empty] | Rev. 12/4/2020
Note on B40: Record the values found before any adjustments, maintenance, or tuning is conducted.

## Example
Southwest Clean Air Agency - Combustion Monitoring Worksheet - O2 Basis
| Facility Name: | XYZ Corporation |  |  | SWCAA ID: | 0542 | Date Performed: | 2018-10-15
| Emission Unit ID: | Boiler #3 |  |  | 1. The CO and NOₓ span gas concentrations must not be less than 50% of the target/permitted pollutant concentration nor more than 200% of the target/permitted pollutant concentration. A lower concentration span gas may be used if it is more representative of measured concentrations. 2. The response check is failed if the difference between the pre-test and post-test readings is greater than 10% of the initial span value. 3. The calibration error check is failed if the pre-test analyzer response to a span or zero gas differs from the span or zero value by more than 10% of the span gas concentration. 4. No more than 12 hours may elapse between the pre-test and post- test analyzer response checks. 5. Calibration and use of an NO₂ cell is required, if: • There are significant quantities of NO₂ expected (e.g., specific types of catalysts, afterburners, etc.), or • The combustion analyzer does not have an integral or supplemental NO₂ to NO converter. 6. Submit results to SWCAA within 15 calendar days of monitoring. 7. Include available documentation of monitoring and quality assurance results such as printouts ("tapes"), data log files, span gas cylinder calibrations, calculations, etc.
| Combust. Unit Manufacturer: | Acme Boiler
| Combust. Unit Model No: | Low Emissions 17
| Combust. Unit Serial No: | 57713
| Burner Manufacturer: | Global Burner
| Burner Model No: | Super Clean 17
| Burner Serial Number: | 12345
| Monitoring Company: | Bob's Boiler Service
| Analyst Name: | Bob Smith
| Test Instrument Make: | Combustion King
| Test Instrument Model: | CK-01
| Fuel Type: | Diesel
| Design Firing Rate: | 25.5 | MMBtu/hr
| Tested Firing Rate: | 20.8 | MMBtu/hr
|  | Time of Pre-Test Calibration: | 10:15
|  | Time of Post-Test Calibration: | 11:00
|  |  | Does the permit have ppm limits for CO and NOₓ? | Yes | 40 CFR 63 Subpart JJJJJJ (Boiler MACT) Monitoring Requirements for Liquid and Solid Fueled Boilers
|  | NOₓ Limit | CO Limit | O₂ Correction |  |  |  |  | Yes | *
Permit Number |  | (ppm) | (ppm) | (%) | Was the burner inspected? |  |  |  | Yes | *
ADP 17-2586 |  | 30 | 50 | 3 | Was the flame pattern inspected and optimized? |  |  |  | Yes | *
[5 empty] | Was the air-to-fuel ratio system operating properly? |  |  |  | Yes | *
Quality Assurance Results |  | NOₓ (ppm) | CO (ppm) | O₂ (%) | Were total CO emissions optimized? |  |  |  | Yes
| Span Concentration: | 101.2 | 55.6 | 20.9 | Describe any maintenance performed on the burner or boiler system in the "Test Notes" section.
| Pre-Test Span Reading: | 95 | 54 | 20.9
| Post-Test Span Reading: | 93 | 52 | 20.8
| Pre-Test Zero Reading: | -0.1 | 0 | 0 | Test Notes:
| Post-Test Zero Reading: | 0 | 0.2 | 0.1
Results (Record at least once every 30 seconds for 5 minutes)
Sample | Stack Temp (°F) | NOₓ Reading (ppm) | CO Reading (ppm) | O₂ Reading (%)
As Found | 341 | 45 | 20 | 2.3
1 | 324 | 29 | 13 | 3
2 | 324 | 28 | 12 | 3.1
3 | 324 | 27 | 13 | 3
4 | 324 | 27 | 14 | 3
5 | 324 | 27 | 15 | 2.9
6 | 324 | 26 | 13 | 3
7 | 324 | 30 | 13 | 3
8 | 324 | 28 | 13 | 3
9 | 324 | 28 | 12 | 3
10 | 324 | 28 | 11 | 3 | NOTIFICATIONS:
11 |  |  |  |  | No Issues Identified. Please remember to include the analyzer printouts and the calibration gas certificates with your submittal.
12
13
14
15
16
17
18
19
20
Test Average | 324 | 27.8 | 12.9 | 3
Drift Corrected Values |  | 29.9673 | 13.4533 | 2.9642
Oxygen Corrected Value |  | 29.9074 | 13.4264
Questions? - Call the Southwest Clean Air Agency at 360-574-3058 | [8 empty] | Rev. 01/10/2019
Note on B40: Record the values found before any adjustments, maintenance, or tuning is conducted.

## Messages
Fail Conditions and Messages
Test # | Condition 1=Fail 0=Pass | Message | FAILURE MESSAGES |  |  | Fuel Types | F-factor | Sort |  | Responses
1 | 0 | • Cell D32 - NOₓ span concentration out of range - see note 1 above - NOₓ results invalid | [6 empty] | <-intentionally left blank |  | <-intentionally left blank
2 | 0 | • Cell E32 - CO span concentration out of range - see note 1 above - CO results invalid |  |  |  | Natural gas | 8710 | 1 |  | Yes
3 | 0 | • Cells D33 & D34 - NOₓ span drift excessive - see note 2 above - NOₓ results invalid |  |  |  | LPG | 8710 | 2 |  | No
4 | 0 | • Cells D35 & D36 - NOₓ zero drift excessive - see note 2 above - NOₓ results invalid |  |  |  | Diesel | 9190 | 3
5 | 0 | • Cells E33 & E34 - CO span drift excessive - see note 2 above - CO results invalid |  |  |  | Fuel Oil No 6 | 9190 | 4
6 | 0 | • Cells E35 & E36 - CO zero drift excessive - see note 2 above - CO results invalid |  |  |  | Alder bark dust | 8611 | 5 |  | Permit Limits?
7 | 0 | • Cells F33 & F34 - O₂ span drift excessive - see note 2 above - O₂ results invalid |  |  |  | Bark | 9600 | 5
8 | 0 | • Cells F35 & F36 - O₂ zero drift excessive - see note 2 above - O₂ results invalid |  |  |  | Coal | 9780 | 5
9 | 0 | • Cell D33 - NOₓ pre-test span reading too high or too low - see note 3 above - NOₓ results invalid |  |  |  | Digester gas | 9450 | 5
10 | 0 | • Cell E33 - CO pre-test span reading too high or too low - see note 3 above - CO results invalid |  |  |  | Gasoline | 9190 | 5
11 | 0 | • Cell F33 - O₂ pre-test span reading too high or too low - see note 3 above - O₂ results invalid |  | Total Fail Messages: | 0 | Hogged fuel | 9600 | 5
12 | 0 | • Cell D35 - NOₓ pre-test zero reading too high or too low - see note 3 above - NOₓ results invalid |  |  |  | Landfill gas | 9450 | 5
13 | 0 | • Cell E35 - CO pre-test zero reading too high or too low - see note 3 above - CO results invalid |  |  |  | LNG | 8710 | 5
14 | 0 | • Cell F35 - O₂ pre-test zero reading too high or too low - see note 3 above - O₂ results invalid |  |  |  | Methane | 8710 | 5
15 | 0 | • Cell F28 - No O₂ correction value has been entered. Enter appropriate O₂ correction value |  |  |  | Butane | 8710 | 5
16 | 0 | • Measured NOₓ exceeds permit limit |  |  |  | Process gas | 9450 | 5
17 | 0 | • Measured CO exceeds permit limit |  |  |  | Propane | 8710 | 5
18 | 0 | • Cell D28 - No NOₓ limit entered |  |  |  | PS300 | 9190 | 5
19 | 0 | • Cell E28 - No CO limit entered |  |  |  | Sander dust | 9240 | 5
20 | 0 | • Cell E28 - NOₓ limit inconsistent with answer in F25 |  |  |  | Wood waste | 9240 | 5
21 | 0 | • Cell E28 - CO limit inconsistent with answer in F25 |  |  |  | Wood waste and sander dust | 9240 | 5
22 | 0 | • Cell F35 - Pre-Test O₂ zero appears to be too high. Assure correct value was entered |  |  |  | Wood/Gas | 9000 | 5
23 | 0 | • Cell F36 - Post-Test O₂ zero appears to be too high. Assure correct value was entered
24 | 0 | • Cell F28 - Check permit for proper O₂ correction, zero is probably not correct
25 | 0 | • Cell F28 - You must enter an O₂ correction, even if you have no permit limit; default for natural gas is 3%.
26 | 0 | • Cell F32 - O₂ span should be either ambient (20.9) or the value of a non-zero O₂ calibration gas
27 | 0 | • Cell F35 - O₂ zero should be determined using your calibration gas (assuming there is no O₂)
28 | 0 | • Temperature data points entered below minimum. Only 0 data point entered.
29 | 0 | • NOₓ data points entered below minimum. Only 0 data point entered.
30 | 0 | • CO data points entered below minimum. Only 0 data point entered.
31 | 0 | • O₂ data points entered below minimum. Only 0 data point entered.
32 | 0 | • Be sure to select whether a permit limit exists or not in Cell F25
33
34
35
36
37
38
39
40